## README
Guide to Use The IOGenerator Engineering Tools
1 | Filling up the excel file and executing the tool:
| 1 | . | Please enter your IO data into EVERY column on the relevant TYPE of the type sheet* (green Sheets).
| 2 | . | Fill the IO data into every column that has the header on row 1. Some column are deliberately hidden for easier use. Headers are explained in section 8
| 3 | . | When excel are filled with IO data, put the EXCEL_MASTER.xlsx file on the same folder as the LOGIC_GENERATOR.exe file
| 4 | . | Execute the LOGIC_GENERATOR.exe
| Note. | : | DON'T REMOVE ANY SHEET OR MODIFY THE ORDER OF THE SHEETS. DON'T MODIFY SHEET HEADER. ONLY MODIFY CELLS/CONTENT OF THE TYPE SHEET
| * |  | These type sheet are:
|  |  |  | Sheet | Type
|  |  | - | DI | Digital Input (NPAS_DI_STS Only)
|  |  | - | DO | Digital Output (NPAS_DO_STS Only)
|  |  | - | AI | Analog Input (NPAS_AI_ANLG Or NPAS_AI_TEMP Only)**
|  |  | - | AO | Analog Output (NPAS_AI_ANLG Only)
|  |  | - | PVI | NPAS_PVI**
|  |  | - | MLD | NPAS_MLD
|  |  | - | PID | NPAS_PID**
|  |  | - | SIO## | NPAS_SIO##
|  |  | - | MASTER | FOR PROGRAM REFERENCE. DON'T MODIFY
If you still do not have any reference to analog range and engineering unit, please DO NOT leave it empty (fill with i.e, 0, 100, and %)
| ** |  | For analog input, please specify ANLG_IN_TYPE with: I_Anlg or I_Temp
2 | Output Files:
| 1 | . | If done correctly, all of the output files will be generate at {.exe directory}/Output folder.
| 2 | . | Those files are:
|  |  | - | DEV_LABEL.csv |  | : This output file is to be imported to DeviceLabelDefinition in logic designer
|  |  | - | LOC_VAR.xlsx |  | : This output file is to be copied to Variable Table of the script POU
|  |  | - | STRUCT_TEXT.txt |  | : This output file is to be copied to worksheet of the script POU
| 3 | . | MASTER.csv is also generated at {.exe directory} and is read by the tool as lines (not to be used for LogicDesigner)
| Note | : | - | Use the MASTER.csv file to debug when the program logs 'Line ## : {errorMessage}'
|  |  | - | If the Output folder is not generated, move the .exe and .xlsx file location in D:/ partition (or where the execution don't need admin previlleges)
3 | Importing DEV_LABEL.csv to DeviceLabelDefinition
| 1 | . | Open Logic Designer
| 2 | . | Open Device Label Definition, and choose 'READING. . .'
| 3 | . | Select DEV_LABEL.csv in the Output folder. Import option can be filled accordingly.
| 4 | . | Continue adding the device label into the project
4 | Copying the Script from STRUCT_TEXT.txt into a new POU
| 1 | . | After creating a new project, insert a program
| 2 | . | Select ST as the language
| 3 | . | Copy all text inside the STRUCT_TEXT.txt file and paste it to the worksheet of the program
| 4 | . | Add the POU into Task
5 | Copying the Local Variables from LOC_VAR.xlsx
After pasting the script into the worksheet, copy all the variables generated into the POU.
| 1 | . | Rearrange the header of the variable table of the POU into --> Name, Type, Desc, Usage, Retain
| 2 | . | Add/append/insert a new variable
| 3 | . | Copy all the variables from LOC_VAR.xlsx
| 4 | . | Paste into the NewVar1. When asked this dialogue, select 'Yes'
| 5 | . | Rebuild the project. By default, there should be 0 error and 0 warning after the rebuild.
| 6 | . | If face with an error, please recheck your EXCEL_MASTER.xlsx for wrong data input
6 | Using 'Source Conversion' Tool in Logic Designer
This tool is meant to be used along with built-in tool 'Source Conversion' in Logic Designer. How to use the 'Conversion Tool':
| 1 | . | After a successful rebuild, right click on the POU and run Logic Designer Conversion Tool to convert ST into FBD language
| 2 | . | Select 'Convert to: FBD' in the radio button. If you select 'Overwrite source POU', the converter will overwrite the script POU
| 3 | . | The converted POU will have several worksheet and each type of NPAS will be separated by comment
| 4 | . | Add the new POU into the Task. Do rearrange as needed since the conversion worksheet will be untidy
7 | Common Error/Warning
| # | . | Permission error
Cause: You perhaps are re-executing LOGIC_GENERATOR and have the output file(s) open.
Solution: Close the file(s) (MASTER.csv/LOC_VAR.xlsx/DEV_LABEL.csv/STRUCT_TEXT.txt).
| # | . | AI Type Wrong Definition at line {idx}. Must be either 'I_Anlg' or 'I_Temp'
Cause: You define data for column 'ANLG_IN_TYPE' wrong. Check affected data at line {idx} on MASTER.csv
Solution: Define data for column 'ANLG_IN_TYPE' with either 'I_Anlg' or 'I_Temp'
| # | . | Line {idx} invalid category. Check MASTER.csv
Cause: You define data for column 'CATEGORY' wrong. Check affected data at line {idx} on MASTER.csv
Solution: Define data for column 'CATEGORY' with: DI/DO/AI/AO/PVI/MLD/PID/SIO22/SIO12/SIO21/SIO11 only
8 | Headers Explanation
This is all the header that might be available when filling data in a TYPE sheet. Not all of them will be needed for a specific type and will deliberately be hidden.
|  | Header |  |  |  | Explanation
| - | CATEGORY |  |  |  | Program reference this data to determine the I/O type
| - | TAG_IN1 |  |  |  | I/O Input Tag 1
| - | DESC_IN1 |  |  |  | Description for I/O Input Tag 1
| - | TAG_IN2 |  |  |  | I/O Input Tag 2 (used in I/O type using more than one input (i.e, SIO22)
| - | DESC_IN2 |  |  |  | Description for I/O Input Tag 2
| - | TAG_OUT1 |  |  |  | I/O Output Tag 1
| - | DESC_OUT1 |  |  |  | Description for I/O Output Tag 1
| - | TAG_OUT2 |  |  |  | I/O Output Tag 2 (used in I/O type using more than one Output (i.e, SIO22)
| - | DESC_OUT2 |  |  |  | Description for I/O Output Tag 2
| - | NPAS_SPECIFIC_NAME |  |  |  | Name for NPAS Specific FB (NPAS_PID, NPAS_SIO##. For NPAS_PVI and MLD use TAG name)
| - | NPAS_SPECIFIC_DESC |  |  |  | Description for NPAS Specific FB
| - | ANLG_IN_TYPE |  |  |  | Analog input type (either I_Anlg for 4-20mA I/O or I_Temp for RTD I/O)
| - | ANLG_IN_RANGE_LO |  |  |  | Analog input low range
| - | ANLG_IN_RANGE_HI |  |  |  | Analog input high range
| - | ANLG_IN_UNIT |  |  |  | Analog input engineering unit
| - | ANLG_OUT_RANGE_LO |  |  |  | Analog Output low range
| - | ANLG_OUT_RANGE_HI |  |  |  | Analog Output high range
| - | ANLG_OUT_UNIT |  |  |  | Analog Output engineering unit

## MASTER
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT

## DI
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT
DI | ESD-000 | ESD PushButton -0
DI | DP-UPS-01B | UPS Indicator
DI | ESD-001 | ESD PushButton -1

## DO
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT
DO |  |  |  |  | ESD-8810 | ESD Command K-8810
DO |  |  |  |  | ESD-8820 | ESD Command K-8820
DO |  |  |  |  | ESD-IND | ESD Indication

## AI
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT
AI | LT-001 | Level Transmitter | [8 empty] | I_Anlg | 0 | 100 | %
AI | TE-001 | Temperature Element | [8 empty] | I_Temp | 20 | 100 | C

## AO
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT
AO |  |  |  |  | CV_001 | Control Valve | [8 empty] | 0 | 100 | %
AO |  |  |  |  | P-001-FRQ | Pump Freq | [8 empty] | 0 | 50 | Hz

## PVI
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT
PVI | PZT-80101 | Pressure Transmitter | [8 empty] | I_Anlg | 0 | 10 | psi
PVI | LZT-80102 | Level Transmitter | [8 empty] | I_Anlg | 0 | 100 | %
PVI | TE-80110 | Temperature Element | [8 empty] | I_Temp | 20 | 100 | C

## MLD
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT
MLD |  |  |  |  | CV-84420 | Control Valve | [8 empty] | 0 | 100 | %
MLD |  |  |  |  | P-002-FRQ | Pump Frequency | [8 empty] | 0 | 50 | Hz

## PID
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT
PID | PT-80001 | Pressure Transmitter |  |  | PCV-80001 | Control Valve |  |  | PCV_80001 | Pressure Control Valve | I_Anlg | 0 | 10 | psi | 0 | 100 | %
PID | TE-80001 | Temperature Element |  |  | TCV-80001 | Control Valve |  |  | TCV_80001 | Temp Control Valve | I_Temp | 20 | 100 | C | 0 | 100 | %

## SIO22
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT
SIO22 | ZSO-84401 | Valve Status Open | ZSC-84401 | Valve Status Close | SVO-84401 | Valve Open Command | SVC-84401 | Valve Close Command | SV_84401 | Solenoid Valve

## SIO12
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT
SIO12 | ZV-84402 | Valve Op/Cl Status |  |  | SVO-84402 | Valve Open Command | SVC-84402 | Valve Close Command | SV-84402 | Solenoid Valve

## SIO21
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT
SIO21 | ZSC-80101 | Valve Close Status - Inlet of Separator SDV-80101 | ZSO-80101 | Valve Open Status - Inlet of Separator SDV-80101 | SDY-80101 | 3-Way SV - Inlet of Separator SDV-80101 |  |  | SDV_80101 | 3-Way SV - Inlet of Separator SDV-80101
SIO21 | ZSC-80102 | Valve Close Status - Gas Outlet of Separator BDV-80102 | ZSO-80102 | Valve Open Status - Gas Outlet of Separator BDV-80102 | BDY-80102 | 3-Way SV - Gas Outlet of Separator BDV-80102 |  |  | BDV_80102 | 3-Way SV - Gas Outlet of Separator BDV-80102
SIO21 | ZSC-80103 | Valve Open Status - Line to HC Liquid Header SDV-80103 | ZSO-80103 | Valve Close Status - Line to HC Liquid Header SDV-80103 | SDY-80103 | 3-Way SV - Line to HC Liquid Header SDV-80103 |  |  | SDV_80103 | 3-Way SV - Line to HC Liquid Header SDV-80103

## SIO11
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT
SIO11 | ZV-84403 | Valve Op/Cl Status |  |  | SV-84403 | Valve Op/Cl Command |  |  | PSV-84403 | Pressure Solenoid Vlv.