## README
Guide to Use The IOGenerator Engineering Tools
1 | Filling up the excel file:
| 1 | . | Please enter your IO data into EVERY column on the relevant TYPE of the type sheet*. DO NOT FILL 'MASTER' SHEET
| 2 | . | Fill the first column with "TYPE" (without " ") on every row that has IO Data. The pre-filled value is set as an example, remove if not needed
| 3 | . | Put the EXCEL_MASTER.xlsx file on the same folder as the LOGIC_GENERATOR.exe file
| 4 | . | Execute the LOGIC_GENERATOR.exe
| Note. | : | DON'T REMOVE ANY SHEET OR MODIFY THE ORDER OF THE SHEETS. ONLY MODIFY CELLS/CONTENT OF THE TYPE SHEET
| * |  | These type sheet are:
|  |  |  | Sheet | Type
|  |  | - | DI | Digital Input (NPAS_DI_STS Only)
|  |  | - | DO | Digital Output (NPAS_DO_STS Only)
|  |  | - | AI | Analog Input (NPAS_AI_ANLG Or NPAS_AI_TEMP Only)**
|  |  | - | AO | Analog Output (NPAS_AI_ANLG Only)
|  |  | - | PVI | NPAS_PVI**
|  |  | - | MLD | NPAS_MLD**
|  |  | - | PID | NPAS_PID**
|  |  | - | SIO## | NPAS_SIO##
If you still do not have any reference to analog range and engineering unit, please DO NOT leave it empty (fill with i.e, 0, 100, and %)
| ** |  | For analog input, please specify ANLG_IN_TYPE with: I_Anlg or I_Temp
2 | Output Files:
| 1 | . | If done correctly, all of the output files will be generate at {.exe directory}/Output folder.
| 2 | . | Those files are:
|  |  | - | DEV_LABEL.csv
|  |  | - | LOC_VAR.xlsx
|  |  | - | STRUCT_TEXT.txt
| 3 | . | MASTER.csv is also generated at {.exe directory} and is read by the LogicGenerator.exe in lines (not to be used for LogicDesigner)
| Note | : | Use the MASTER.csv file to debug when the program mention 'Line ## : invalid category'
If the Output folder is not generated, move the .exe and .xlsx file location in D:/ partition (or where the execution don't need admin previlleges)
3 | Importing DEV_LABEL.csv to DeviceLabelDefinition
| 1 | . | Open Logic Designer
| 2 | . | Open Device Label Definition, and choose 'READING. . .'
| 3 | . | Select DEV_LABEL.csv in the Output folder. Import option can be filled accordingly.
| 4 | . | Continue adding the device label into the project
4 | Copying the Script from STRUCT_TEXT.txt into a new POU
| 1 | . | After creating a new project, insert a program
| 2 | . | Select ST as the language
| 3 | . | Copy all text inside the STRUCT_TEXT.txt file and paste it to the worksheet of the program
| 4 | . | Add the POU into Task
5 | Copying the Local Variables from LOC_VAR.xlsx
| 0 | . | After pasting the script into the worksheet, copy all the variables generated into the POU.
| 1 | . | Rearrange the header of the variable table of the POU into --> Name, Type, Desc, Usage, Retain
| 2 | . | Add/append/insert a new variable
| 3 | . | Copy all the variables from LOC_VAR.xlsx
| 4 | . | Paste into the NewVar1. When asked this dialogue, select 'Yes'
| 5 | . | Rebuild the project. By default, there should be 0 error and 0 warning after the rebuild.
| 6 | . | If face with an error, please recheck your EXCEL_MASTER.xlsx for wrong data input
6 | Using 'Source Conversion' Tool in Logic Designer
| 1 | . | After a successful rebuild, right click on the POU and run Logic Designer Conversion Tool to convert ST into FBD language
| 2 | . | Select 'Convert to: FBD' in the radio button. If you select 'Overwrite source POU', the converter will overwrite the script POU
| 3 | . | The converted POU will have several worksheet and each type of NPAS will be separated by comment
| 4 | . | Add the new POU into the Task. Do rearrange as needed since the conversion file is untidy
7 | Common Error/Warning
| # | . | Permission error
Cause: You perhaps are re-executing LOGIC_GENERATOR and have the output file(s) open.
Solution: Close the file(s) (MASTER.csv/LOC_VAR.xlsx/DEV_LABEL.csv/STRUCT_TEXT.txt).
| # | . | AI Type Wrong Definition at line {idx}. Must be either 'I_Anlg' or 'I_Temp'
Cause: You define data for column 'ANLG_IN_TYPE' wrong. Check affected data at line {idx} on MASTER.csv
Solution: Define data for column 'ANLG_IN_TYPE' with either 'I_Anlg' or 'I_Temp'
| # | . | Line {idx} invalid category. Check MASTER.csv
Cause: You define data for column 'CATEGORY' wrong. Check affected data at line {idx} on MASTER.csv
Solution: Define data for column 'CATEGORY' with: DI/DO/AI/AO/PVI/MLD/PID/SIO22/SIO12/SIO21/SIO11 only
| # | . | If im still here, please report your error to: faishal.tahsiin@yokogawa.com cc: ferdian.pradana@yokogawa.com with subject: LOGIC_GENERATOR_ERR

## MASTER
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT

## DI
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT
DI | ESD-000 | ESD Push Button from ESS Existing Panel Train #2
DI | DP-UPS-01B | UPS Indicator
DI | ESD-001 | ESD-PB 1 - Gas Compressor Area - North of Overhaul Area
DI | ESD-002 | ESD-PB 2 - Filter Area - South Fence Near Hydrant
DI | MCC-ON | MCC GBC (New Elec Room) Status ON
DI | MCC-TRIP | MCC GBC (New Elec Room) Status TRIP
DI | MCC-ALRM | MCC GBC (New Elec Room) Status ALARM
DI | PSD-81001 | Process Shutdown from K-8100
DI | PSD-82001 | Process Shutdown from K-8200
DI | PSD-83001 | Process Shutdown from K-8300
DI | PSD-84001 | Process Shutdown from K-8400
DI | PSD-85001 | Process Shutdown from K-8500
DI | PSD-86001 | Process Shutdown from K-8600
DI | ESD-PB | ESD Push Button from ESS Panel
DI | PSD-000 | PSD Push Button from ESS Existing Panel Train #2
DI | PSD-PB | PSD Push Button from ESS Panel

## DO
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT
DO |  |  |  |  | ESD-8810 | ESD Command K-8810
DO |  |  |  |  | ESD-8820 | ESD Command K-8820
DO |  |  |  |  | ESD-IND | ESD Indication To Existing ESS Control Panel
DO |  |  |  |  | XL-001A | Strobe Light 1A - Office Area
DO |  |  |  |  | XA-001 | Horn 1 - Office Area
DO |  |  |  |  | XL-001B | Strobe Light 1B - Office Area
DO |  |  |  |  | XL-002A | Strobe Light 2A - Field Area
DO |  |  |  |  | XA-002 | Horn 2 - Field Area
DO |  |  |  |  | XL-002B | Strobe Light 2B - Field Area
DO |  |  |  |  | MCC-ESD-01 | Utility - MCC Trip Command
DO |  |  |  |  | MCC-ESD-02 | DP-UPS - MCC Trip Command 1/2
DO |  |  |  |  | MCC-ESD-03 | DP-UPS - MCC Trip Command 2/2
DO |  |  |  |  | MCC-ESD-04 | Crane Shelter Gas Comp - MCC Trip Command
DO |  |  |  |  | MCC-ESD-05 | i/A - MCC Trip Command 1/2
DO |  |  |  |  | MCC-ESD-06 | i/A - MCC Trip Command 2/2
DO |  |  |  |  | MCC-ESD-07 | Demin Water - MCC Trip Command
DO |  |  |  |  | MCC-ESD-08 | Waste Trf Pump - MCC Trip Command
DO |  |  |  |  | MCC-ESD-09 | N2 Gen - MCC Trip Command
DO |  |  |  |  | GAS-COMP-TRIP | Gas Compressor Signal Trip to Aux Panel in Existing Control Room
DO |  |  |  |  | P-5030-STA | P-5030 Start Signal to Aux Panel Train # 2

## AI
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT

## AO
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT

## PVI
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT
PVI | PZT-80101 | PT - Separator V-8010 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | LZT-80102 | LT - Separator V-8010 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | LZT-80302 | LT - Discharge Gas Scrubber V-8030 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | PZT-80403 | PT - Out Gas to Exist Amine Plant Line P-8042-DS-10" | [8 empty] | I_Anlg | 0 | 100 | %
PVI | PT-80702 | PT - Inlet of FG Filter Coalescer | [8 empty] | I_Anlg | 0 | 100 | %
PVI | PT-80901 | PT - Instrument Air Receiver V-8090 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | GD-001 | Gas Detector 1 - K-8100 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | GD-002 | Gas Detector 2 - K-8200 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | GD-003 | Gas Detector 3- K-8300 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | GD-004 | Gas Detector 4 - K-8400 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | GD-005 | Gas Detector 5 - K-8500 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | GD-006 | Gas Detector 6 - K-8600 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | GD-007 | Gas Detector 7 - Fuel Gas Filter Area F-8070A/B | [8 empty] | I_Anlg | 0 | 100 | %
PVI | GD-008 | Gas Detector 8 - Discharge Gas Filter F-8040A/B | [8 empty] | I_Anlg | 0 | 100 | %
PVI | GD-009 | Gas Detector 9 - Suction Gas Filter F-8020A/B | [8 empty] | I_Anlg | 0 | 100 | %
PVI | GD-001-H2S | H2S Gas Detector 1 - K-8100 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | GD-002-H2S | H2S Gas Detector 2 - K-8200 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | GD-003-H2S | H2S Gas Detector 3 - K-8300 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | GD-004-H2S | H2S Gas Detector 4 - K-8400 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | GD-005-H2S | H2S Gas Detector 5 - K-8500 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | GD-006-H2S | H2S Gas Detector 6 - K-8600 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | GD-007-H2S | H2S Gas Detector 7 - Fuel Gas Filter Area F-8070A/B | [8 empty] | I_Anlg | 0 | 100 | %
PVI | GD-008-H2S | H2S Gas Detector 8 - Discharge Gas Filter F-8040A/B | [8 empty] | I_Anlg | 0 | 100 | %
PVI | GD-009-H2S | H2S Gas Detector 9 - Suction Gas Filter F-8020A/B | [8 empty] | I_Anlg | 0 | 100 | %
PVI | FD-001 | Flame Detector 1 - North Fence K-8100/8200 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | FD-002 | Flame Detector 2 - South Fence K-8100/8200 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | FD-003 | Flame Detector 3 - North Fence K-8300/8400 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | FD-004 | Flame Detector 4 - South Fence K-8300/8400 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | FD-005 | Flame Detector 5 - North Fence K-8500/8600 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | FD-006 | Flame Detector 6 - South Fence K-8500/8600 | [8 empty] | I_Anlg | 0 | 100 | %
PVI | FD-007 | Flame Detector 7 - West Fence Filter Area | [8 empty] | I_Anlg | 0 | 100 | %
PVI | FD-008 | Flame Detector 8 - South Fence Filter Area | [8 empty] | I_Anlg | 0 | 100 | %
PVI | FD-009 | Flame Detector 9 - East Fence Filter Area | [8 empty] | I_Anlg | 0 | 100 | %
PVI | FD-010 | Flame Detector 10 - North Fence Filter Area | [8 empty] | I_Anlg | 0 | 100 | %

## MLD
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT

## PID
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT

## SIO22
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT

## SIO12
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT

## SIO21
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT
SIO21 | ZSC-80101 | Valve Close Status - Inlet of Separator SDV-80101 | ZSO-80101 | Valve Open Status - Inlet of Separator SDV-80101 | SDY-80101 | 3-Way SV - Inlet of Separator SDV-80101 |  |  | SDV_80101 | 3-Way SV - Inlet of Separator SDV-80101
SIO21 | ZSC-80102 | Valve Close Status - Gas Outlet of Separator BDV-80102 | ZSO-80102 | Valve Open Status - Gas Outlet of Separator BDV-80102 | BDY-80102 | 3-Way SV - Gas Outlet of Separator BDV-80102 |  |  | BDV_80102 | 3-Way SV - Gas Outlet of Separator BDV-80102
SIO21 | ZSC-80103 | Valve Open Status - Line to HC Liquid Header SDV-80103 | ZSO-80103 | Valve Close Status - Line to HC Liquid Header SDV-80103 | SDY-80103 | 3-Way SV - Line to HC Liquid Header SDV-80103 |  |  | SDV_80103 | 3-Way SV - Line to HC Liquid Header SDV-80103

## SIO11
CATEGORY | TAG_IN1 | DESC_IN1 | TAG_IN2 | DESC_IN2 | TAG_OUT1 | DESC_OUT1 | TAG_OUT2 | DESC_OUT2 | NPAS_SPECIFIC_NAME | NPAS_SPECIFIC_DESC | ANLG_IN_TYPE | ANLG_IN_RANGE_LO | ANLG_IN_RANGE_HI | ANLG_IN_UNIT | ANLG_OUT_RANGE_LO | ANLG_OUT_RANGE_HI | ANLG_OUT_UNIT